# EC medium pressure axial fan
Sizes 1120 to 1600

Direct-drive EC medium pressure axial fan with high-performance axial impeller with hub, mounted on a GreenTech EC external rotor motor with integrated control electronics.

Double-flange housing made of galvanised sheet steel, flow-optimised nozzle shape on inlet side, corrosion protection as per DIN EN ISO 12944, class C5 M; transport loops for safe handling during shipping and installation.

Impeller and hub made of die-cast aluminium, with flow-optimised Airfoil blade geometry, blade angle and number of blades specified at the factory to suit the required operating point; installation possible on inlet or pressure side; motorised impeller balanced in two planes (static and dynamic) as per DIN ISO 1940 to balance quality G 6.3. 
GreenTech EC external rotor motor surpasses efficiency class IE4, magnets without use of rare earths, maintenance-free ball bearings with long-term lubrication, theoretical nominal service life of at least 40,000 operating hours, installation with horizontal and vertical motor shaft; soft start, integrated current limitation, wide input voltage range 3-phase 380-480 V, 50/60 Hz, fan suitable for use with all standard power supply systems with no effect on air performance.

Compact electronics; no need to install shielded wiring; extremely low-noise commutation logic; 100% speed control, with PID controller; RS485/MODBUS RTU interface; pre-set operating parameters, no parametrisation work required.

Terminal box made of aluminium with readily accessible connection area with spring terminals, environment-resistant cable glands.

Any work required to prevent the transmission of structure-borne noise is to be performed by the customer.

Fan satisfies the relevant EMC regulations and requirements with regard to circuit feedback; documentation and marking conform to the applicable EU directives. 
Reliable performance data, air performance measurements on inlet-side chamber test rig in accordance with ISO 5801 and DIN 24163, noise measurements in low-reflection acoustic test chamber as per DIN EN ISO 3745.

# Integrated protective devices:

- Alarm relay with floating contacts (250 V AC/2 A, cos φ = 1)

- Locked-rotor protection

- Phase failure detection

- Motor soft start

- Mains undervoltage detection

- Excess temperature protection for electronics and motor

- Short circuit protection

# Optional:

- Different and specific requirements on request

Technical data:

Fan types 		W3G ________ - ________ - _____

Air flow 	qV	= ___________________________	m3/h

Stat. pressure increase	pfs	= ___________________________	Pa

Stat. overall efficiency	ηes	= ___________________________	%

Operating speed	n	= ___________________________	min-1

Motor type		= EC motor

Type of control		= 0-100% speed control

Motor efficiency class 		= IE4

Total power consumption	Ped	= ___________________________	kW

Specific fan power	SFP	= ___________________________	kW/(m³/s)

Nominal voltage range 	UN	= ___________________________	V

Mains frequency	f	= 50 / 60	Hz

Nominal current	IN	= ___________________________	A

Ingress protection		= IP54

Sound power level	LW A(A, in)	= _______ / LWA(A, out) = _______	dB(A)

Sound pressure level (at 1 m)	LpA(A, in)	= _______ / LpA(A, out) = _______	dB(A)

Perm. ambient temperature	T	= ____________ to ____________	°C

Fan mass 	m	= ___________________________	kg

# Product photo

EC axial fan – straight blades W3G…

# Refer to data sheet for dimensions and connections