# RadiCal DC centrifugal fans
Sizes 190 to 280

Direct-drive, single inlet centrifugal fans with backwards-curved high-performance centrifugal impellers with radial diffusors, based on a GreenTech EC external rotor motor with integrated control electronics.

Impeller made of glass-fiber reinforced plastic, with backwards-curved blades, manufactured in one piece without seams.
Motor impeller statically and dynamically balanced on two planes to balancing grade G 6.3 in accordance with DIN ISO 1940.
GreenTech EC external rotor motor surpasses efficiency class IE4, magnets with no rare earths, maintenance-free ball bearings (sealed) with long-term lubrication, theoretical nominal service life of at least 40,000 hours of operation, installation with horizontal and vertical motor shaft; soft start, integrated current limitation. Voltage range 8-16 V, 16-28 V, 36-57 V; Integrated electronics, quiet commutation logic; 100 % speed controllable; control signal 0-10 V DC / PWM; tach output.
Cable connection with protruding, pre-assembled, variable cable, with wire-end ferrules, UV-resistant, water impermeable.
Any work required for isolation from structure-borne noise to be performed by the customer. 
Fan satisfies the applicable EMC guidelines and requirements with regard to circuit feedback; documentation and marking conform to the applicable EU Directives. UL 507 approval. 
Reliable performance data, air performance measurements in intake-side test chamber according to ISO 5801 and DIN 24163, sound measurements in an anechoic test chamber in accordance with DIN EN ISO 3745.

# Integrated protective devices:

- Reverse polarity and locked-rotor protection

- Overvoltage detection

- Soft start

- Motor current limitation

- Thermal overload protection

# Optional:

- Other and specific requirements on request

# Technical data:

Fan type 		R1G ________ - ________ - _____

Air flow 	qV	= ___________________________	m3/h

Actual pressure increase	pfs	= ___________________________	Pa

Overall static efficiency	ηed	= ___________________________	%

Operating speed	n	= ___________________________	rpm

Motor type		= DC motor

Control type		= 0-10 VDC, 0-100% PWM

Motor efficiency class		= IE4

Total power consumption	Ped	= ___________________________	kW

Specific fan power	SFP	= ___________________________	kW/(m³/s)

Nominal voltage range 	UN	= ___________________________	V

Nominal current	IN	= ___________________________	A

Protection class 		= IP 24 KM (motor); electronics IP 66/69 K

Sound power level	LW A(A, in)	= _______ / LWA(A, out) = _______	dB(A)

Sound pressure level (at 1 m)	LpA(A, in)	= _______ / LpA(A, out) = _______	dB(A)

Permitted ambient temperature	T	= _______________ to _______________	°C

Weight of fan 	m	= ___________________________	kg

# Product photo

RadiCal DC centrifugal fans

# For dimensions and connections, see data sheet