# EC centrifugal fans – RadiFit 
Sizes 250 to 400

Direct-drive dual-inlet centrifugal fans with backward-curved high-performance centrifugal impellers mounted on a GreenTech EC external rotor motor with add-on control electronics. 
Scroll housing made of galvanised sheet steel with bolted-on adjustable mounting bracket, optimised step diffuser in discharge for low-noise operation, connection flange on pressure side. 
Aluminium impeller with 7 backward-curved, offset, continuously welded blades. Flow-optimised inlet nozzle made of galvanised sheet steel. 
Motorised impeller balanced in two planes (static and dynamic) as per DIN ISO 1940 to balance quality G 6.3. 
GreenTech EC external rotor motor surpasses efficiency class IE4, magnets without use of rare earths, maintenance-free ball bearings with long-term lubrication, theoretical nominal service life of at least 40,000 operating hours, soft start, integrated current limitation, wide input voltage range 3-phase 380-480 V, 50/60 Hz, fan suitable for use with all standard power supply systems with no effect on air performance. Motorised impeller isolated from surroundings with specially designed vibration-absorbing elements, compact electronics, aluminium housing, low-noise commutation logic; 100% speed control; PID controller; RS485/MODBUS RTU interface, no need for shielded wiring. 
Readily accessible connection area with spring terminals, cable entry can be moved through 180 degrees, environment-resistant cable glands. 
Fan satisfies the relevant EMC regulations and requirements with regard to circuit feedback; documentation and marking conform to the applicable EU directives. 
Reliable performance data, air performance measurements on inlet-side chamber test rig in accordance with ISO 5801 and DIN 24163, noise measurements in low-reflection acoustic test chamber as per DIN EN ISO 3745.

# Integrated protective devices:

- Alarm relay with floating contacts (250 V AC/2 A, cos φ = 1)

- Locked-rotor protection

- Phase failure detection

- Motor soft start

- Mains undervoltage detection

- Excess temperature protection for electronics and motor

- Short circuit protection

# Optional:

- Different requirements on request

# Technical data:

Fan types 		D3G ________ - ________ - _____

Air flow 	qV	= ___________________________	m3/h

Stat. pressure increase	pfs	= ___________________________	Pa

Stat. overall efficiency	ηes	= ___________________________	%

Operating speed	n	= ___________________________	min-1

Motor type		= EC motor

Type of control		= 0-100% speed control

Motor efficiency class 		= IE4

Total power consumption	Ped	= ___________________________	kW

Specific fan power	SFP	= ___________________________	kW/(m³/s)

Nominal voltage range 	UN	= ___________________________	V

Mains frequency	f	= 50 / 60	Hz

Nominal current	IN	= ___________________________	A

Ingress protection		= IP54

Sound power level	LW A(A, in)	= _______ / LWA(A, out) = _______	dB(A)

Sound pressure level (at 1 m)	LpA(A, in)	= _______ / LpA(A, out) = _______	dB(A)

Perm. ambient temperature	T	= ____________ to ____________	°C

Fan mass 	m	= ___________________________	kg

# Product photo

EC centrifugal fans – RadiFit D3G400

# Refer to data sheet for dimensions and connections